## UART OR RS485
1.Convention
Interface | UART/RS485
baud rate | 115200 bps
communication format | 115200, N, 8, 1
data format | motorola
Master | PC
Slave | BMS
2.1PC Request Slave Data Format
Item | data | description | byte Num. | remark
0 | Frame header | Frame_header_H | 1 | 0xAA
1 |  | Frame_header_L | 1 | 0xBB
2 | Rack_ID |  | 1
3 | Shelf_ID |  | 1
4 | CMD |  | 1 |  | CMD
5 | Data_Num |  | N | the number of data1~dataN | CMD | description
6 | data1 |  | 1 |  | 0x01 | Summary&detail information
7 | data2 |  | 1 |  | 0x02 | Cell Temperature
8 | data3 |  | 1 |  | 0x03 | Cell voltage
9 | data4 |  | 1 |  | … | …
10 | data5 |  | 1 |  | 0x10 | Driver Manual control
11 | data6 |  | 1 |  | 0x11 | all parameter read
12 | data7 |  | 1 |  | 0x12 | Parameter set
13 | data8 |  | 1 |  | 0x13 | SOC_Set
14 | CRC16 | CRC16_H | 1 |  | 0x14 | RTC_Set
15 |  | CRC16_L | 1 |  | … | …
16 | Frame end | Frame_end_H | 1 | 0xCC | … | …
17 |  | Frame_end_L | 1 | 0xDD | 0x20 | EEPROM log data read
[5 empty] | … | …
2.2.Slave responds to Master Data Format |  |  |  |  | 0xFF | Rack_ID
Item | data | description | byte Num. | remark
0 | Frame header | Frame_header_H | 1 | 0x11
1 |  | Frame_header_L | 1 | 0x22
2 | Rack_ID |  | 1
3 | Shelf_ID |  | 1
4 | CMD |  | 1
5 | Data_Num |  | N | the number of data1~dataN
6 | data1
7 | data2
8 | …
9 | …
10 | data N-1
11 | data N
12 | CRC16 | CRC16_H | 1
13 |  | CRC16_L | 1
14 | Frame end | Frame_end_H | 1 | 0x33
15 |  | Frame_end_L | 1 | 0x44
3. Summary information
DATA | description | Resolution/Offset | Example
data1 | TotalVol_1 | 0.1V | 345.6V: 3456
data2
data3 | TotalVol_2 | 0.1V
data4
data5 | TotalVol_3 | 0.1V
data6
data7 | Current | 0.1A/-1000A/Current by Hall sensor. Chrge_current is positive | Chg30A： 300+10000 DisChg30A: -300+10000
data8
data9 | MaxVol | 1mV
data10
data11 | MaxVolID
data12 | MinVol | 1mV
data13
data14 | MinVolID
data15 | MaxTemp | 1°C/-40°C
data16 | MaxTempID
data17 | MinTemp | 1°C/-40°C
data18 | MinTempID
data19 | warning_pre | bit0:Cell_OV bit1:Battery_OV bit2:Chg_OCur bit3:Chg_UTemp bit4:Chg_OTemp bit5:Cell_UV bit6:Battery_UV bit7:DisChg_OCur bit8:DisChg_UTemp bit9:DisChg_OTemp bit10:SOC_Low bit11:V_Diff bit12:T_Diff bit13:internal CAN Commu fault bit14:Main positive contactor stuck fault bit15:Main negative contactor stuck fault bit16:Precharge contactor stuck fault bit17:Main positive contactor open fault bit18:Main negative contactor open fault bit19:Precharge contactor open fault bit20:precharge fault bit21: FAN cooling fault bit22:TM4C-to-MSP430 SPI fault bit23:MSP430-to-BQ79600 SPI fault
data20
data21
data22
data23 | warning
data24
data25
data26
data27 | fault
data28
data29
data30
data31 | Drive_Status | bit0: MPC_Stat,Main positive contactor status bit1: MNC_Stat,Main negative contactor status bit2: PCC_Stat,Precharge contactor status bit3: LED1_Stat bit4: LED2_Stat bit5: LED3_Stat bit6: LED4_Stat bit7: FAN1_Stat bit8: FAN2_Stat bit9: FAN3_Stat 0:disable 1:enable
data32
data33 | Input_Status | bit0:Lock 0:disable 1:enable
data34 | Bat_Status | 0000:stand by, 0001:charge 0010:discharge 0011:precharge_in 0100:precharge_out， 0101:full charge
data35 | SOC
data36 | SOH
data37 | BalanceVol | 1mV
data38
data39 | MBB1_Balance_Stas | bit0~bit10: cell1~cell11 balance sta 0:enable 1:disable
data40
data41 | MBB2_Balance_Stas | bit0~bit10: cell1~cell11 balance sta 0:enable 1:disable
data42
data43 | MBB3_Balance_Stas | bit0~bit10: cell1~cell11 balance sta 0:enable 1:disable
data44
data45 | MBB4_Balance_Stas | bit0~bit10: cell1~cell11 balance sta 0:enable 1:disable
data46
data47 | MBB5_Balance_Stas | bit0~bit10: cell1~cell11 balance sta 0:enable 1:disable
data48
data49 | MBB6_Balance_Stas | bit0~bit10: cell1~cell11 balance sta 0:enable 1:disable
data50
data51 | FW version
data52
data53 | HW version
data54
data55 | RTC_Y | Y=year-2000
data56 | RTC_MON
data57 | RTC_D
data58 | RTC_H
data59 | RTC_MIN
data60 | RTC_S
… | …
data80 | RESERVED
4.cell voltage
DATA | description | Resolution/Offset | Example
data1 | Cell_Vol_1 | 1mV
data2
… | …
… | …
data131 | Cell_Vol_66 | 1mV
data132
5. Cell Temperature
DATA | description | Resolution/Offset | Example
data1 | Cell_Temp_1 | 1°C/-40°C
data2 | Cell_Temp_2 | 1°C/-40°C
… | … | 1°C/-40°C
… | … | 1°C/-40°C
data24 | Cell_Temp_24 | 1°C/-40°C
data25 | Balance_Temp_1 | 1°C/-40°C
data26 | Balance_Temp_2 | 1°C/-40°C
… | … | 1°C/-40°C
… | … | 1°C/-40°C
data30 | Balance_Temp_6 | 1°C/-40°C
data31 | Die_Temp_1 | 1°C/-40°C
data32 | Die_Temp_2 | 1°C/-40°C
… | … | 1°C/-40°C
… | … | 1°C/-40°C
data42 | Die_Temp_12 | 1°C/-40°C
6.Driver Manual control: PC data
DATA | description | Resolution/Offset | Example
data1 | Driver | bit0:Main positive contactor bit1:Main negative contactor bit2:PreChg contactor bit3:LED1 bit4:LED2 bit5:LED3 bit6:LED4 bit7:FAN1 bit8:FAN2 bit9:FAN3
data2
data3 | action | 1:enable 0:disable
data4 | RESERVED | 1
data5 | RESERVED | 1
data6 | RESERVED | 1
Driver Manual control: BMS data
DATA | description | Resolution/Offset | Example
data1 | result | 1:Y 0:N
7.Parameter set: PC data
DATA | description | Resolution/Offset | Example
data1 | Parameter ID | refer to Parameter ID sheet
data2
data3 | parameter value
data4
data5
data6
data7
data8
parameter set: BMS data
DATA | description | Resolution/Offset | Example
data1 | Parameter ID | refer to Parameter ID sheet
data2
data3 | result | 1:Y 0:N
8. parameter read: PC data
DATA | description | Resolution/Offset | Example
data1 | Parameter ID | refer to Parameter ID sheet: 0x50（threshhold value） 0x51（calibration value） 0x52（factory vaule）
data2
data3 | RESERVED
data4 | RESERVED
data5 | RESERVED
data6 | RESERVED
data7 | RESERVED
data8 | RESERVED
threshhold value parameter read: BMS data
DATA | description | Resolution/Offset | Example
data1 | Value(Parameter ID==0x01)
data2
data3 | Value(Parameter ID==0x02)
data4
data5 | Value(Parameter ID==0x03)
data6
data7 | …
data8
data7 | Value(Parameter ID==0x27)
data 78
calibration value parameter read: BMS data
data 1 | Value(Parameter ID==0xA0)
data 2
… | …
…
data 15 | Value(Parameter ID==0xA7)
data 16
factory vaule parameter read: BMS data
data 1 | Cell_Type | 1:NCM/NCA, 2:LFP, 3:LMO, 4:LTO
data 2 | Cell_Parallel_Config | 并联数，5P
data 3 | Shelf_Serial_Config | 电芯串数，66S
data 4 | Cell_Temperature_Config | 24S
data 5 | Rated_Capacity | 0.1Ah，额定容量
data 6
data 7 | Rated_Voltage | 0.1V，额定电压
data 8
data 9 | BMS_SN
data 10
data 11
data 12
data 13 | Project_Code
data 14
data 15
data 16
data 17 | Voltage_Platform | 电压使用平台，1：208V，2：400V/480V
9. RTC Set: PC data
DATA | description | Resolution/Offset | Example
data1 | Parameter ID | refer to Parameter ID sheet: 0xF3
data2
data3 | Y | year-2000
data4 | Mon
data5 | D
data6 | H
data7 | Min
data8 | S
RTC Set: BMS data
DATA | description | Resolution/Offset | Example
data1 | Parameter ID | refer to Parameter ID sheet
data2
data3 | result | 1:Y 0:N
11. SOC set: PC data
DATA | description | Resolution/Offset | Example
data1 | Parameter ID | refer to Parameter ID sheet: 0xF2
data2
data3 | SOC
data4 | RESERVED
data5 | RESERVED
data6 | RESERVED
data7 | RESERVED
data8 | RESERVED
SOC Set: BMS data
DATA | description | Resolution/Offset | Example
data1 | Parameter ID | refer to Parameter ID sheet
data2
data3 | result | 1:Y 0:N
12. Rack ID set: PC data
DATA | description | Resolution/Offset | Example
Frame header | Frame_header_H | 1 | 0xAA
| Frame_header_L | 1 | 0xBB
Rack_ID | 0xFF | 1
Shelf_ID | 0xFF | 1
CMD | 0xFF | 1
Data_Num | 8 | N | the number of data1~dataN
data1 | Rack ID
data2 | RESERVED
data3 | RESERVED
data4 | RESERVED
data5 | RESERVED
data6 | RESERVED
data7 | RESERVED
data8 | RESERVED
CRC16 | CRC16_H | 1
| CRC16_L | 1
Frame end | Frame_end_H | 1 | 0xCC
| Frame_end_L | 1 | 0xDD
Rack ID Set: BMS data
DATA | description | Resolution/Offset | Example
data1 | Parameter ID | refer to Parameter ID sheet
data2
data3 | result | 1:Y 0:N

## Parameter ID
Parameter ID | Parameter Item | Parameter Value Format/Resolution/Offset
0x01 | Cell_OV_Warning_Pre | 1mV
0x02 | Cell_OV_Warning | 1mV
0x03 | Cell_OV_Fault | 1mV
0x04 | Battery_OV_Warning_Pre | 0.1V
0x05 | Battery_OV_Warning | 0.1V
0x06 | Battery_OV_Fault | 0.1V
0x07 | Chg_OCur_Warning_Pre | 0.1A
0x08 | Chg_OCur_Warning | 0.1A
0x09 | Chg_OCur_Fault | 0.1A
0xA | Chg_Utemp_Warning_Pre | 1°C/-40°C
0xB | Chg_Utemp_Warning | 1°C/-40°C
0xC | Chg_Utemp_Fault | 1°C/-40°C
0xD | Chg_Otemp_Warning_Pre | 1°C/-40°C
0xE | Chg_Otemp_Warning | 1°C/-40°C
0xF | Chg_Otemp_Fault | 1°C/-40°C
0x10 | Cell_UV_Warning_Pre | 1mV
0x11 | Cell_UV_Warning | 1mV
0x12 | Cell_UV_Fault | 1mV
0x13 | Battery_UV_Warning_Pre | 0.1V
0x14 | Battery_UV_Warning | 0.1V
0x15 | Battery_UV_Fault | 0.1V
0x16 | DisChg_OCur_Warning_Pre | 0.1A
0x17 | DisChg_OCur_Warning | 0.1A
0x18 | DisChg_OCur_Fault | 0.1A
0x19 | DisChg_UTemp_Warning_Pre | 1°C/-40°C
0x1A | DisChg_UTemp_Warning | 1°C/-40°C
0x1B | DisChg_UTemp_Fault | 1°C/-40°C
0x1C | DisChg_Otemp_Warning_Pre | 1°C/-40°C
0x1D | DisChg_Otemp_Warning | 1°C/-40°C
0x1E | DisChg_Otemp_Fault | 1°C/-40°C
0x1F | SOC_Low_Warning_Pre | 1%
0x20 | SOC_Low_Warning | 1%
0x21 | SOC_Low_Fault | 1%
0x22 | V_Diff_Warning_Pre | 1mV
0x23 | V_Diff_Warning | 1mV
0x24 | V_Diff_Fault | 1mV
0x25 | T_Diff_Warning_Pre | 1°C
0x26 | T_Diff_Warning | 1°C
0x27 | T_Diff_Fault | 1°C
… | …
0x4F | All parameter
0x50 | 读取threshhold value
0x51 | 读取calibration value
0x52 | 读取factory vaule
… | …
0xA0 | TotalVol_1_Slope
0xA1 | TotalVol_1_Offset
0xA2 | TotalVol_2_Slope
0xA3 | TotalVol_2_Offset
0xA4 | TotalVol_3_Slope
0xA5 | TotalVol_3_Offset
0xA6 | Current_Slope
0xA7 | Current_Offset
0xA8 | SOC_Set
0xA9 | RTC_Set | Y-Mon-D-H-Min-S，Y=year-2000
… | …
0xE0 | Cell_Type | 1:NCM/NCA, 2:LFP, 3:LMO, 4:LTO
0xE1 | Cell_Parallel_Config | 并联数，5P
0xE2 | Shelf_Serial_Config | 电芯串数，66S
0xE3 | Cell_Temperature_Config | 24S
0xE4 | Rated_Capacity | 额定容量
0xE5 | Rated_Voltage | 额定电压
0xE6 | BMS_SN | 暂定4个字节
0xE7 | Project_Code | 项目代码，4个字节，e.g.7705928
0xE8 | Voltage_Platform | 电压使用平台，1：208V，2：400V/480V
… | …
0xF0 | Rack_ID | 1～3

## bootloader
Interface | UART | Data Format
Baud Rate | 115200bps | ByteNum | CheckSum | data0 | data1 | … | dataN
communication format | 115200, N, 8, 1 | number of data bytes to send | data CheckSum
Program Address Offset | 0x4000(16k) | eg: Send a 0x20 PING command, the data frame is：0x03 0x20 0x20
Reset MCU After Program | Yes
Download file type | .bin
bootloader Download process
CMD |  | shake hands: 1.PC sends PING command: 03 20 20 2.BMS replies with ACK：00 CC Sending program address and .bin file size: 3.PC sends DOWNLOAD command: 0B DE 21 00 00 40 00 00 00 09 74 4.BMS replies with ACK：00 CC 5.PC sends COMMAND_GET_STATUS：03 23 23 CC 6.BMS replies：00 CC 03 40 40 Send .bin file data: 7.PC sends SEND_DATA：Num CK 24 xx xx xx 8.BMS replies with ACK：00 CC 9.PC sends COMMAND_GET_STATUS：03 23 23 CC 10.BMS replies：00 CC 03 40 40 11.The cycle is sent to the .bin data transmission is completed. Reset: 12.After the bin data is sent, sendCOMMAND_RESET： 03 25 25 13.BMS replies with ACK: 00 CC
COMMAND_PING,0x20
COMMAND_DOWNLOAD,0x21
COMMAND_RUN,0x22
COMMAND_GET_STATUS,0x23
COMMAND_SEND_DATA,0x24
COMMAND_RESET,0x25
COMMAND_ACK,0xCC
COMMAND_NAK,0x33

## APM2.0 bootloader
1. Convention
| Interface | UART or RS485
| Baud Rate | 115200bps
| communication format | 115200, N, 8, 1
| data format | Modbus RTU
| Master | PC
| Slave | BMS
| Version | V0.1
2. Modbus标准数据格式
|  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
| Read | Send | 从站地址 | 功能码03 | start add |  | 寄存器数 |  | CRC_L | CRC_H
|  | receive | 从站地址 | 功能码03 | 字节数 | 寄存器值 |  | CRC_L | CRC_H
| Write | Send | 从站地址 | 功能码10 | start add |  | 寄存器数量N |  | 写入字节数2N | 写入值 | CRC_L | CRC_H
|  | receive | 从站地址 | 功能码10 | start add |  | 寄存器数量N |  | CRC_L | CRC_H
3. APM2.0锂电bootloader通信协议
1 | 握手，读6020寄存器状态，确认进入boot | PC | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 3 | 60 | 20 | 0 | 1 | CRC_L | CRC_H
|  | Bat | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 3 | 2 | ACK/NAK |  | CRC_L | CRC_H
2 | 选择刷写芯片，写6019寄存器，选择MSP430/TM4C | PC | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 10 | 60 | 19 | 00 | 01 | 2 | MSP430/TM4C | CRC_L | CRC_H
|  | Bat | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 10 | 60 | 19 | 00 | 01 | CRC_L | CRC_H
3 | 读BMS状态，读6023寄存器 | PC | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 3 | 60 | 23 | 0 | 1 | CRC_L | CRC_H
|  | Bat | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 3 | 2 | Status |  | CRC_L | CRC_H
4 | 发送下载文件的大小及每包发送数据的大小，写6021寄存器 | PC | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 10 | 60 | 21 | 00 | 03 | 6 | 下载文件的大小Size |  |  |  | 每包发送数据字节数n | CRC_L | CRC_H
|  | Bat | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 10 | 60 | 21 | 00 | 03 | CRC_L | CRC_H
5 | 读BMS状态，读6023寄存器 | PC | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 3 | 60 | 23 | 0 | 1 | CRC_L | CRC_H
|  | Bat | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 3 | 2 | Status |  | CRC_L | CRC_H
6 | 发送下载数据，写6024寄存器 | PC | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 10 | 60 | 24 | 00 | n/2 | n | data0 | … | datan | CRC_L | CRC_H
|  | Bat | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 10 | 60 | 24 | 00 | n/2 | CRC_L | CRC_H
7 | 读BMS状态，读6023寄存器 | PC | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 3 | 60 | 23 | 0 | 1 | CRC_L | CRC_H
|  | Bat | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 3 | 2 | Status |  | CRC_L | CRC_H
8 | 循环发送下载数据，同步骤6-7，至下载完成 | …
9 | 下载完成，读6025寄存器 | PC | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 10 | 60 | 25 | 0 | 1 | CRC_L | CRC_H
|  | Bat | RackID(bit7~bit5)+ShlefID(bit4~bit0) | 10 | 2 | ACK/NAK |  | CRC_L | CRC_H
寄存器功能表
| 序号 | 寄存器 | bar: 0
| 1 | 0x6019 | 0: 选择芯片，TM4C：1，MSP430：2
| 2 | 0x6020 | 0: 握手，此命令用于接收来自引导加载程序的确认信息，表明通信已经建立。成功ACK: 0xCC, 不成功NAK：0x33。
| 3 | 0x6021 | 0: 此命令用于发送下载文件的大小（4字节）及每包发送数据的大小（2字节）；此命令后需要查询BMS回复的状态（0x6023），以确保程序大小和数据包大小是有效的。
| 4 | 0x6023 | 0: 此命令用于查询BMS的状态，返回的Status状态值的定义如下。 COMMAND_RET_SUCCESS 0x40 COMMAND_RET_UNKNOWN_CMD 0x41 COMMAND_RET_INVALID_CMD 0x42 COMMAND_RET_INVALID_ADD 0x43 COMMAND_RET_FLASH_FAIL 0x44
| 4 | 0x6024 | 0: 此命令用于连续发送下载数据；此命令后需要查询BMS回复的状态(0x6023)，以确保程序大小和数据包大小是有效的。
| 5 | 0x6025 | 0: 此命令用于指示下载完成，成功ACK: 0xCC, 不成功NAK：0x33